Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Section by any end user. A qualified design professional should review and edit the document to suit Project.

SECTION 232300 - REFRIGERANT PIPING

- GENERAL

Verify with equipment specifications refrigeration components that are supplied and edit this Section as needed.

      - SUMMARY

        - Section Includes:

          - Part 2 ACR Copper Press for Refrigerant Piping Applications.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of ACR Copper Press Fittings.

          - Include material description, fabrication methods, and accessories required for installation.

        - Shop Drawings:

          - Include attachment details, attachment to other work, if any, and operational clearances.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Engineer, but they do not require Engineer's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For qualified Installer.

Retain "Field Quality-Control Reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field Quality-Control Reports: For each field quality control test and inspection.

      - CLOSEOUT SUBMITTALS

        - Maintenance Data: For each type of product, including related accessories.

      - QUALITY ASSURANCE

Retain "Installer Qualifications" Paragraph below if Contractor is required to assume responsibility for installing of fittings.

        - Installer Qualifications:

          - Pressure-Seal Joining Procedure for Copper Piping. Qualify operators in accordance with training provided by respective manufacturer.

      - DELIVERY, STORAGE, AND HANDLING

        - Comply with ACR Copper Press Fittings manufacturers' written instructions for minimum and maximum temperature and humidity requirements for shipment, storage, and handling.

        - Deliver ACR Copper Press Fittings materials in unopened bundles and store in a temperature-controlled dry place with adequate air circulation.

        - Store ACR Copper Press Fittings and protect material from damage prior to installation.

      - FIELD CONDITIONS

Retain this article if interruption of existing sprinkler service is required.

        - Interruption of Existing Refrigerant Piping Service: Do not interrupt refrigerant piping service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary refrigerant piping service in accordance with requirements indicated:

          - Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of refrigerant piping service.

          - Do not proceed with interruption of refrigerant piping service without [Architect's] [Construction Manager's] [Owner's] written permission.

- PRODUCTS

      - PERFORMANCE REQUIREMENTS

        - Refrigerant Piping and components should be in accordance with ASHRAE 15 and ASME B31.5.

If more than one type of refrigerant is required for Project, retain applicable paragraphs below and indicate on Drawings which piping circuit requires which refrigerant.

See comments regarding line test pressures in "Refrigerant Piping Design Considerations" Article in the Evaluations. Test pressures may require adjustment to accommodate unusual system operating temperatures or other extreme conditions.

        - Test Pressure for Refrigerant R-134a:

          - Suction Tubing Refrigeration and Air-Conditioning Applications Other than Heat Pumps: [115 psig (793 kPa)] <Insert pressure>.

          - Suction Tubing for Heat-Pump Applications: [225 psig (1551 kPa)] <Insert pressure>.

          - Hot-Gas and Liquid Tubing: [225 psig (1551 kPa)] <Insert pressure>.

        - Test Pressure for Refrigerant R-407C:

          - Suction Tubing for Refrigeration and Air-Conditioning Applications Other than Heat Pumps: [230 psig (1586 kPa)] <Insert pressure>.

          - Suction Tubing for Heat-Pump Applications: [380 psig (2620 kPa)] <Insert pressure>.

          - Hot-Gas and Tubing Lines: [380 psig (2620 kPa)] <Insert pressure>.

        - Test Pressure for Refrigerant R-410A:

          - Suction Tubing for Refrigeration and Air-Conditioning Applications Other than Heat Pumps: [300 psig (2068 kPa)] <Insert pressure>.

          - Suction Tubing for Heat-Pump Applications: [535 psig (3689 kPa)] <Insert pressure>.

          - Hot-Gas and Tubing Lines: [535 psig (3689 kPa)] <Insert pressure>.

      - REFRIGERANT PIPING SPECIALTIES

        - Streamline® ACR Copper Press Fittings:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provided by Mueller Streamline Co.; Streamline® ACR Copper Press:

            - <Insert manufacturer's name>.

          - Description: Streamline® ACR copper press fittings for use in HVAC and VRF applications. Available sizes ranging from 1/4 to 1-1/8 inches (10 to 29 mm) in diameter. Product is designed to join ASTM B280 and ASTM B88 hard drawn copper tube (Types ACR, K, and L) from 1/4 to 1-1/8 inches (10 to 29 mm) as well as ASTM B280 and ASTM B1003 soft copper tube up to 7/8 inch (22 mm).

          - Standards:

            - ASTM B280.

            - ASTM B88.

            - ASTM B1003.

          - Maximum Operating Pressure: 700 psi (48 bar).

          - Operating Temperature: Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

          - Material: UNS C12200 minimum 99.9 percent pure copper for the body.

          - Sealing Ring Temperature Rating: Minus 40 to plus 300 deg F (Minus 40 to plus 149 deg C).

          - Sealing Element: HNBR.

          - Sizes: 1/4 to 1-1/8 inches (10 to 29 mm).

        - Underground Burial Tape:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

3M Scotchrap® Tape 50 and Shurtape® PW100 are comparable impermeable coating systems designed to protect joints from moisture, debris, corrosion, and other soil stresses.

          - Basis-of-Design Product: Subject to compliance with requirements, provide 3M; [Scotchrap Tape 50] [or] [Shurtape PW100] or comparable product.

            - <Insert manufacturer's name>.

        - Tool and Compression Jaws Compatibility:

          - Pipe sizes 1/4 to 1-1/8 inches (10 to 29 mm):

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

            - Basis-of-Design Product: Subject to compliance with requirements, provide Milwaukee® Streamline® ACR Press Jaws Series or comparable product.

              - <Insert manufacturer's name>.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

            - Basis-of-Design Product: Subject to compliance with requirements, provide [Dewalt® Full Sized DCE200M2] [Hilti Full Sized NPR 32-A] [Klauke® UAP] [Milwaukee®; M18™ FORCE LOGIC™ 2922-20] [Milwaukee®; M18™ Long Throw 2773-20L] [REMS Full Sized 579011] [REMS Full Sized 579010] [REMS Full Sized 571014] [REMS Full Sized 576011] [REMS Full Sized 576010] [REMS Full Sized 577010] [REMS Full Sized 57211] [Ridgid® RP300] [Ridgid® 320-E] [Ridgid® RP330-B] [Ridgid® RP 330-C] [Ridgid® RP340] [Ridgid® RP 350] [Rothenberger ROMAX® 3000] [Rothenberger ROMAX® 4000] [Rothenberger ROMAX® AC ECO] Series or comparable product.

              - <Insert manufacturer's name>.

- EXECUTION

If more than one refrigerant is required for Project, retain appropriate refrigerant piping (tubing) articles below and indicate refrigerant type for each pipe/tube indicated on Drawings.

      - PIPING APPLICATION SCHEDULES

        - Refrigerant: [R-134a] [R-407C] [R-410A]

Retain first paragraph below to require all suction, hot-gas, and liquid tubing for conventional air-conditioning (cooling-only) applications to be Type ACR, annealed temper. Type ACR, annealed-temper tubing is available only in sizes NPS 1-1/2 (DN 40) and smaller. Retain second paragraph if tube sizes exceed NPS 1-1/2 (DN 40) and it is desirable to have all tubing be of same tube type and joining method. Retain first and third paragraphs to require tubing NPS 2 (DN 50) and larger to be different from the NPS 1-1/2 (DN 40) and smaller Type ACR, annealed temper.

        - Suction, Hot-Gas, and Liquid Tubing for Conventional Air-Conditioning (Cooling-Only) Applications, NPS 1-1/2 (DN 40) and Smaller: Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

        - Suction, Hot-Gas, and Liquid Tubing for Conventional Air-Conditioning (Cooling-Only) Applications, NPS 4 (DN 100) and Smaller: Copper, [Type ACR] [Type L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

        - Suction, Hot-Gas, and Liquid Tubing for Conventional Air-Conditioning (Cooling-Only) Applications, NPS 2 to NPS 4 (DN 50 to DN 100): Copper, [Type ACR] [Type L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

Retain one of first two paragraphs below.

        - Safety-Relief-Valve Discharge Tubing for Conventional Air-Conditioning (Cooling-Only) Applications, Copper: [Type ACR] [Type K (A)] [or] [Type L (B)], [drawn-temper] [or] [annealed-temper] tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

        - Safety-Relief-Valve Discharge Piping for Conventional Air-Conditioning (Cooling-Only) Applications, Steel: Schedule 40, black steel and wrought-steel fittings with welded joints.

Retain first paragraph below to require all suction, hot-gas, and liquid tubing for heat-pump applications to be Type ACR, annealed temper. Type ACR, annealed-temper tubing is available only in sizes NPS 1-1/2 (DN 40) and smaller. Retain second paragraph if tube sizes exceed NPS 1-1/2 (DN 40) and it is desirable to have all piping be of same tube type and joining method. Retain first and third paragraphs to require piping NPS 2 (DN 50) and larger to be different from the NPS 1-1/2 (DN 40) and smaller Type ACR, annealed temper.

        - Suction, Hot-Gas, and Liquid Tubing for Heat-Pump Applications, NPS 1-1/2 (DN 40) and Smaller: Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

        - Suction, Hot-Gas, and Liquid Tubing for Heat-Pump Applications, NPS 4 (DN 100) and Smaller: Copper, [Type ACR] [Type L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

        - Suction, Hot-Gas, and Liquid Tubing for Heat-Pump Applications, NPS 2 to NPS 4 (DN 50 to DN 100): Copper, [Type ACR] [Type L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

Retain one of first two paragraphs below.

        - Safety-Relief-Valve Discharge Tubing for Heat-Pump Applications, Copper: [Type ACR] [Type K (A)] [or] [Type L (B)], [drawn-temper] [or] [annealed-temper] tubing and wrought-copper fittings with [brazed] [or] [soldered] joints

        - Safety-Relief-Valve Discharge Piping for Heat-Pump Applications, Steel: Schedule 40, black steel and wrought-steel fittings with welded joints.

      - VALVE AND SPECIALTY APPLICATIONS

Delete first paragraph below if valves are specified in Section 236200 "Packaged Compressor and Condenser Units."

        - Install service valves for gage taps at inlet and outlet of hot-gas bypass valves and strainers if they are not an integral part of valves and strainers.

Retain first paragraph below if suction line will be exposed to air temperatures of less than 75 deg F (24 deg C) during compressor operation.

        - Install a check valve at the compressor discharge and a liquid accumulator at the compressor suction connection.

        - Except as otherwise indicated, install [diaphragm packless] [packed-angle] valves on inlet and outlet side of filter dryers.

Retain first paragraph below only for systems that cannot be shut down for a short time to replace the filter dryer.

        - Install a full-size, three-valve bypass around filter dryers.

Retain first paragraph below for solenoid valves on systems with multiple thermostatic expansion valves. Retain for hot-gas bypass valve if not integral to the valve.

        - Install solenoid valves upstream from each expansion valve and hot-gas bypass valve. Install solenoid valves in horizontal lines with coil at top.

        - Install thermostatic expansion valves as close as possible to distributors on evaporators.

          - Install valve so diaphragm case is warmer than bulb.

In first subparagraph below, verify proper location for bulb with valve manufacturer.

          - Secure bulb to clean, straight, horizontal section of suction line using two bulb straps. Do not mount bulb in a trap or at bottom of the line.

          - If external equalizer lines are required, make connection where it will reflect suction-line pressure at bulb location.

        - Install safety-relief valves where required by ASME Boiler and Pressure Vessel Code. Pipe safety-relief-valve discharge line to outside in accordance with ASHRAE 15.

        - Install moisture/liquid indicators in liquid line at the inlet of the thermostatic expansion valve or at the inlet of the evaporator coil capillary tube.

        - Install strainers upstream from and adjacent to the following unless they are furnished as an integral assembly for the device being protected:

Revise subparagraphs below for equipment required for Project.

          - Solenoid valves.

          - Thermostatic expansion valves.

          - Hot-gas bypass valves.

          - Compressor.

        - Install filter dryers in liquid line between compressor and thermostatic expansion valve[, and in the suction line at the compressor].

Consult refrigeration equipment manufacturer to determine the need for a receiver.

        - Install receivers sized to accommodate pump-down charge.

See the Evaluations for discussion of flexible connectors.

        - Install flexible connectors at compressors.

        - Provide refrigerant locking caps on refrigerant charging ports that are located outdoors unless otherwise protected from unauthorized access by a means acceptable to authority having jurisdiction.

      - INSTALLATION OF PIPING, GENERAL

        - Soldering or Brazing Near an Existing Press Connection:

          - Brazing near Streamline® ACR Press Fittings should be avoided. The installer should take precautions to keep the press connection cool. The following methods may include.

            - Wrapping the press connection with a cold wet cloth.

            - Fabricating solder connections prior to installing the press fitting.

            - Applying heat barrier spray, gels, or putty to avoid heat transfer to the press fitting.

        - Pressing Near an Existing Soldered or Brazed Connection:

          - No foreign debris or residual brazing on the tubing to be inserted into the Streamline® ACR Press fitting.

          - The surface condition on the area of press joint should be clean and free from debris in accordance with ASTM B280 or ASTM B88 Type K or Type L copper.

          - The area of the braze joint to be cooled down before insertion.

        - Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems; indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations. Install piping as indicated unless deviations to layout are approved on Shop Drawings.

        - Install refrigerant piping in accordance with ASHRAE 15.

        - Install piping in concealed locations unless otherwise indicated and except in equipment rooms and service areas.

        - Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless specifically indicated otherwise.

        - Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

        - Install piping adjacent to machines to allow service and maintenance.

        - Install piping free of sags and bends.

        - Install ACR Press fittings for changes in direction and branch connections.

        - Select system components with pressure rating equal to or greater than system operating pressure.

        - Refer to Section 230923 "Direct Digital Control (DDC) System for HVAC" and Section 230993.11 "Sequence of Operations for HVAC DDC" for solenoid valve controllers, control wiring, and sequence of operation.

        - Install piping as short and direct as possible, with a minimum number of joints, elbows, and fittings.

        - Arrange piping to allow inspection and service of refrigeration equipment. Install valves and specialties in accessible locations to allow for service and inspection. Install access doors or panels as specified in Section 083113 "Access Doors and Frames" if valves or equipment requiring maintenance is concealed behind finished surfaces.

        - Install refrigerant piping in protective conduit where installed belowground.

        - Install refrigerant piping in rigid or flexible conduit in locations where exposed to mechanical injury.

        - Slope refrigerant piping as follows:

See the Evaluations for discussion of oil entrainment. Refer to the ASHRAE HANDBOOK - "Refrigeration" for discussion of methods for managing oil entrainment in refrigerant gas and liquid.

          - Install horizontal hot-gas discharge piping with a uniform slope downward away from compressor.

          - Install horizontal suction lines with a uniform slope downward to compressor.

Use double-suction riser for maximum compressor efficiencies if load variation is expected.

          - Install traps and double risers to entrain oil in vertical runs.

          - Liquid lines may be installed level.

Retain first paragraph below for steel pipe. Review the cost of steel pipe using these procedures versus the cost of copper piping. Also consider limiting the size of the refrigerant system and its piping to avoid the use of steel pipe.

        - Before installation of steel refrigerant piping, clean pipe and fittings using the following procedures:

          - Shot blast the interior of piping.

          - Remove coarse particles of dirt and dust by drawing a clean, lintless cloth through tubing by means of a wire or electrician's tape.

          - Draw a clean, lintless cloth saturated with trichloroethylene through the tube or pipe. Continue this procedure until cloth is not discolored by dirt.

          - Draw a clean, lintless cloth, saturated with compressor oil, squeezed dry, through the tube or pipe to remove remaining lint. Inspect tube or pipe visually for remaining dirt and lint.

          - Finally, draw a clean, dry, lintless cloth through the tube or pipe.

          - Safety-relief-valve discharge piping is not required to be cleaned but is required to be open to allow unrestricted flow.

        - Install piping with adequate clearance between pipe and adjacent walls and hangers or between pipes for insulation installation.

        - Identify refrigerant piping and valves in accordance with Section 230553 "Identification for HVAC Piping and Equipment."

        - Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

        - Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

        - Install escutcheons for piping penetrations of walls, ceilings, and floors. Comply with requirements for escutcheons specified in Section 230518 "Escutcheons for HVAC Piping."

      - JOINT CONSTRUCTION

        - Install ACR Copper Press couplings, nipples, and transition and special fittings that have finish and pressure ratings same as or higher than system's pressure rating for aboveground applications unless otherwise indicated.

        - Minimum distance between press joints pressing near an existing press connection:

          - 1/4 inch (10 mm) pipe size; 1/4 inch (7 mm) minimum distance required.

          - 3/8 inch (12 mm) pipe size; 1/4 inch (7 mm) minimum distance required.

          - 1/2 inch (15 mm) pipe size; 1/4 inch (7 mm) minimum distance required.

          - 5/8 inch (18 mm) pipe size; 1/4 inch (7 mm) minimum distance required.

          - 3/4 inch (20 mm) pipe size; 1/4 inch (7 mm) minimum distance required.

          - 7/8 inch (22 mm) pipe size; 1/4 inch (7 mm) minimum distance required.

          - 1-1/8 inch (29 mm) pipe size; 1/4 inch (7 mm) minimum distance required.

        - Minimum distance for soldering or brazing near an existing press connection:

          - Soldering:

            - 1/4 inch (10 mm) pipe size; 1-1/2 inch (76 mm) minimum distance required.

            - 3/8 inch (12 mm) pipe size; 1-1/2 inch (76 mm) minimum distance required.

            - 1/2 inch (15 mm) pipe size; 1-1/2 inch (76 mm) minimum distance required.

            - 5/8 inch (18 mm) pipe size; 1-1/2 inch (76 mm) minimum distance required.

            - 3/4 inch (20 mm) pipe size; 2-1/4 inch (57 mm) minimum distance required.

            - 7/8 inch (22 mm) pipe size; 3 inch (76 mm) minimum distance required.

            - 1-1/8 inch (26 mm) pipe size; 4 inch (102 mm) minimum distance required.

          - Brazing:

            - 1/4 inch (10 mm) pipe size; 5 inch (127 mm) minimum distance wet wrapped.

            - 3/8 inch (12 mm) pipe size; 5 inch (127 mm) minimum distance wet wrapped.

            - 1/2 inch (15 mm) pipe size; 5 inch (127 mm) minimum distance wet wrapped.

            - 5/8 inch (18 mm) pipe size; 6 inch (152 mm) minimum distance wet wrapped.

            - 3/4 inch (20 mm) pipe size; 7 inch (178 mm) minimum distance wet wrapped.

            - 7/8 inch (22 mm) pipe size; 8 inch (203 mm) minimum distance wet wrapped.

            - 1-1/8 inch (26 mm) pipe size; 11 inch (279 mm) minimum distance wet wrapped.

            - 1/4 inch (10 mm) pipe size; 10 inch (254 mm) minimum distance unprotected.

            - 3/8 inch (12 mm) pipe size; 10 inch (254 mm) minimum distance unprotected.

            - 1/2 inch (15 mm) pipe size; 10 inch (254 mm) minimum distance unprotected.

            - 5/8 inch (18 mm) pipe size; 12 inch (305 mm) minimum distance unprotected.

            - 3/4 inch (20 mm) pipe size; 14 inch (356 mm) minimum distance unprotected.

            - 7/8 inch (22 mm) pipe size; 16 inch (406 mm) minimum distance unprotected.

            - 1-1/8 inch (26 mm) pipe size; 22 inch (559 mm) minimum distance unprotected.

        - Pressing near and existing soldered or brazed connection:

          - 1/4 inch (10 mm) pipe size; 3 inch (76 mm) minimum distance required.

          - 3/8 inch (12 mm) pipe size; 3 inch (76 mm) minimum distance required.

          - 1/2 inch (15 mm) pipe size; 3 inch (76 mm) minimum distance required.

          - 5/8 inch (18 mm) pipe size; 3 inch (76 mm) minimum distance required.

          - 3/4 inch (20 mm) pipe size; 3 inch (76 mm) minimum distance required.

          - 7/8 inch (22 mm) pipe size; 3 inch (76 mm) minimum distance required.

          - 1-1/8 inch (29 mm) pipe size; 3 inch (76 mm) minimum distance required.

        - Ream ends of pipes and tubes and remove burrs. Bevel plain ends of steel pipe.

        - Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

Retain first paragraph below for copper pipe.

        - Fill pipe and fittings with an inert gas (nitrogen or carbon dioxide), during brazing or welding, to prevent scale formation.

        - Soldered Joints: Construct joints in accordance with ASTM B828 or CDA's "Copper Tube Handbook."

        - Brazed Joints: Construct joints in accordance with AWS BRH, "Brazing Handbook," Ch. 35, "Pipe and Tubing."

          - Use Type BCuP (copper-phosphorus) alloy for joining copper socket fittings with copper pipe.

          - Use Type BAg (cadmium-free silver) alloy for joining copper with bronze or steel.

        - Threaded Joints: Thread steel pipe with tapered pipe threads in accordance with ASME B1.20.1. Cut threads full and clean using sharp dies. Ream threaded pipe ends to remove burrs and to restore full ID. Join pipe fittings and valves as follows:

          - Apply appropriate tape or thread compound to external pipe threads unless dry-seal threading is specified.

          - Damaged Threads: Pipe or pipe fittings with threads that are corroded or damaged, cracked, or have open welds are unacceptable.

        - Steel pipe can be threaded, but threaded joints must be seal brazed or seal welded.

        - Welded Joints: Construct joints in accordance with AWS D10.12M/D10.12.

        - Flanged Joints: Select appropriate gasket material, size, type, and thickness for service application. Install gasket concentrically positioned. Use suitable lubricants on bolt threads.

      - INSTALLATION OF HANGERS AND SUPPORTS

Retain first paragraph below for projects in areas that require seismic restraints.

        - Comply with requirements for seismic restraints in Section 230548 "Vibration and Seismic Controls for HVAC."

        - Comply with Section 230529 "Hangers and Supports for HVAC Piping and Equipment" for hangers, supports, and anchor devices.

        - Install the following pipe attachments:

          - Adjustable steel clevis hangers for individual horizontal runs less than 20 ft. (6 m) long.

          - Roller hangers and spring hangers for individual horizontal runs 20 ft. (6 m) or longer.

          - Pipe Roller: MSS SP-58, Type 44 for multiple horizontal piping 20 ft. (6 m) or longer, supported on a trapeze.

          - Spring hangers to support vertical runs.

          - Copper-clad hangers and supports for hangers and supports in direct contact with copper pipe.

        - Install hangers for [copper tubing] [and] [steel piping], with maximum horizontal spacing and minimum rod diameters, to comply with MSS SP-58, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Support horizontal piping within [12 inches (300 mm)] <Insert dimension> of each fitting.

        - Support vertical runs of [copper tubing] [and] [steel piping] to comply with MSS SP-58, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

      - FIELD QUALITY CONTROL

Retain first option in "Testing Agency" Paragraph below if Owner hires an independent testing agency.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Tests and Inspections" Paragraph below to require Contractor to perform tests and inspections.

        - Tests and Inspections:

          - Comply with ASME B31.5, Chapter VI.

          - Test refrigerant piping, specialties, and receivers. Isolate compressor, condenser, evaporator, and safety devices from test pressure if they are not rated above the test pressure.

          - Test high- and low-pressure side piping of each system separately at not less than the pressures indicated in "Performance Requirements" Article.

            - Fill system with nitrogen to the required test pressure.

            - System must maintain test pressure at the manifold gage throughout duration of test.

            - Test joints and fittings with electronic leak detector or by brushing a small amount of soap and glycerin solution over joints.

            - Remake leaking joints using new materials, and retest until satisfactory results are achieved.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Prepare test and inspection reports.

      - SYSTEM CHARGING

        - Charge system using the following procedures:

          - Install core in filter dryers after leak test but before evacuation.

          - Evacuate entire refrigerant system with a vacuum pump to 500 micrometers (67 Pa). If vacuum holds for 12 hours, system is ready for charging.

          - Break vacuum with refrigerant gas, allowing pressure to build up to 2 psig (14 kPa).

          - Charge system with a new filter-dryer core in charging line.

      - ADJUSTING

Retain first paragraph below for adjustable thermostatic expansion valves.

        - Adjust thermostatic expansion valve to obtain proper evaporator superheat.

        - Adjust high- and low-pressure switch settings to avoid short cycling in response to fluctuating suction pressure.

        - Adjust set-point temperature of air-conditioning or chilled-water controllers to the system design temperature.

        - Perform the following adjustments before operating the refrigeration system, in accordance with manufacturer's written instructions:

          - Open shutoff valves in condenser water circuit.

          - Verify that compressor oil level is correct.

          - Open compressor suction and discharge valves.

          - Open refrigerant valves but not bypass valves that are used for other purposes.

          - Check open compressor-motor alignment and verify lubrication for motors and bearings.

        - Replace core of replaceable filter dryer after system has been adjusted and after design flow rates and pressures are established.

END OF SECTION 232300